## Power
Electrical Utility Service Agreement Data Sheet
This form provides basic information for the WSDOT Region Utilities Office and the Serving Electrical Utility for one electrical service connection and the equipment being supported by that connection. The information on this form can normally be used to support completion of Utility application forms.
Instructions for filling out this form are available in WSDOT Roadside Electrical and Electronic Systems (REES) Standard E1, Roadside Power Distribution, Section E1.4(4)(b): Basic Service Agreement Information.
Location Information
1 | WSDOT Service Agreement #: | SB 0246
2 | Service Request Type: | New Service Connection
3 | Connection Type: | Aerial (Overhead)
4 | State Route: | Interstate 90
5 | Service Location: | Interstate 90 EB Off-Ramp at Road O NE
6 | Nearest Searchable Address: | 396 Road O NE, Moses Lake, WA 98837 (Bing Maps)
7 | Approximate SRMP: | 182.87
8 | Serving Utility: | Grant County PUD #2
9 | Existing Utility Account Number: | ##########
Service Cabinet Information
10 | Service Voltage: | 120V/240V Single Phase
11 | Service Demand Load (kVA): | 5
12 | Service Panel Type: | WSDOT Modified Type B
13 | Service Main Breaker Size (Amps): | 20
Proposed Service Connection Wiring
14 | Wire Size: | #6
15 | Wire Type | Copper, USE/USE-2
16 | Number of Conductors: | 3
Additional Site Information
17 | Equipment Served: | X | Roadway Lighting
Traffic Signal(s)
Intelligent Transportation System(s)
Other:
18 | Requested Point of Service: | Existing overhead transformer #????? on pole #???????.
19 | Description: | WSDOT is removing and replacing the existing service cabinet. Request disconnect from existing service cabinet and connection to new replacement service cabinet.
20 | Special Instructions: | None
v2022.11.18
Items on grey background are for reference and form functionality only - they do not print.
Request Type
New Service Connection
Disconnect/Reconnect
Customer Load Increase
Disconnect and Removal
Connection Type
Underground
Aerial (Overhead)
Voltages
120V/240V Single Phase
480V Single Phase
480V/277V Three Phase
Service Panel Types
Temporary Commercial
WSDOT Type A
WSDOT Type B
WSDOT Modified Type B
WSDOT Type C
WSDOT Type D
WSDOT Type E
| Main Breaker |  |  | Feeder Size
| 20 |  |  | #6
| 40 |  |  | #6
| 60 |  |  | #6
| 80 |  |  | #4
| 100 |  |  | #3
| 125 |  |  | #2
| 150 |  |  | #1/0
| 175 |  |  | #2/0
| 200 |  |  | #3/0
| 225 |  |  | #4/0
| 250 |  |  | #4/0
| 300 |  |  | 300 kcmil
| 350 |  |  | 400 kcmil
| 400 |  |  | 500 kcmil
Feeder size per NEC Table 310.16. Next larger size used when wire and breaker ampacities match. Utility min size #6.
Wire Types
Copper, USE/USE-2
Aluminum Triplex
Aluminum USE/USE-2
Utilities
Alder Mutual Light Co.
Avista
Benton PUD
Benton Rural Electric Association
Big Bend Electric Co-Op
Chelan County PUD
City of Blaine
City of Cheney
City of Dupont
City of Milton
City of Port Angeles
City of Richland
City of Sumas
Clallam County PUD #1
Clark Public Utilities
Clearwater Power
Columbia REA
Cowlitz County PUD #1
Douglas County PUD
Elmhurst Mutual Power & Light Co.
Ferry County PUD #1
Franklin County PUD
Grant County PUD #2
Grays Harbor PUD
Inland Power and Light
Jefferson County PUD
Joint Base Lewis-McChord
Kittitas PUD #1
Klickitat PUD
Lakeview Light & Power
Lewis County PUD
Mason County PUD #1
Mason County PUD #3
McCleary Light & Power
Nespelem Valley Electric Co-Op
Ohop Mutual Light Co.
Okanogan County Electric Co-Op
Okanogan PUD #1
Pacific County PUD #2
Pacific Power
Parkland Light & Water
Pend Oreille PUD
Peninsula Light Co.
Puget Sound Energy
Seattle City Light
Skamania PUD #1
Snohomish PUD
Tacoma Power
Town of Eatonville
<- Enter Utility Name here if not on list
| Wahkiakum PUD | User entered name will show up in drop-down.
Whatcom PUD #1
Note on D42: Jackson, Flint: Warning: This cell is not locked to allow for manual override of wire size if directed by Utility.